## Sheet1 (hidden)
Inputs
Is the main greater or equal to 8"
Is the main grp or upvc
Will there be any other mains greater or equal to 8" in the excavation
Is the main greater or equal to 4bar
Is the work planned to be undertaken on (or in the vicinity of) a live.
Can the main be depressurised
type of work (eg. Tapping)
depth
location (impact of flooding, schools, basements, railway line).
Have we conclusively proved that the we know the main we are working on.
concrete surrpund or proximity to thrust restraints
Outputs
level of sign of required/ authorisation | low, med | is level 7
extent of RAMS eg. Specific contigency plan | high risk | Chris Featherstone.
SSOW
requirement for valve checks
requirement for full isolation.
shut pack
Pass to CD?
Low | Local sign off. Network Analyst, Risk Assessor
Medium | NOE plus senior manager within delivery organisation.
High | NOE, Senior Manager within delivery organisation and SLT sign off.

## RISK ASSESSMENT
Operational Risk Assessment
| Severity/Consequence Questions | Pick from dropdown | [7 empty] | Score | [10 empty] | Risk Assessment Comments | Guidance |  |  | a | Yes
nst question on eform | Is public safety at risk if the main were to burst during the work. (schools, basements, railway lines, underground)? |  | 0 | [6 empty] | 0 | [14 empty] | b | No
nst view on eform | What control measures be in place to mitigate the risk of flooding in the event of failure? |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0 | [11 empty] | c | Don't know
risk assessor | Will the main be isolated or abandoned? |  | 1 | [6 empty] | 5 | [14 empty] | d | N/a
risk assessor | If not can the main be depressurised? |  | 0 | [6 empty] | -20 | [11 empty] | This question asks if the main / sewer can be depressurised because if it can, then this will reduce the risk to people working on it. If the main / sewer cannot be depressurised additional works will need to be completed to ensure the safety of people working on it. |  |  | e
nst view | Have we proved that the main can be shut in in the event of failure? |  | 0 | [6 empty] | 5 | [11 empty] | A qualifying question which is simply answered "Yes" or "No" at the time of the Risk Assessment. This might change prior to works starting but is important so the correct Safe System Of Work can be designed in the event of catastrophic failure. If the answer is "No", think about the subsequent controls.
| If the main were to burst during excavation/ repair would there be any risk/ damage to third party assets/services (eg.substations, HV/LV mains, gas mains). |  | 0 | [6 empty] | 5 | [11 empty] | Remember this is a template document not a specific risk assessment. If the answer is "No", then the score is 0 and thus doesn't cause an increase in risk score. When the answer is "Yes", then this identifies that there is potential to damage 3rd party equipment and that could increase the risk to public safety. If that is the case, appropriate controls must be identified during the risk assessment and then put in place and manged throughout the work. These control measures could include isolation or diversion.
risk assessor | Is there a known leakage or burst history associated with the main being worked on or in close proximity to the work? |  | 0 | [6 empty] | 0
risk assessor view | At what depth is the main? |  | 0 | 0 | 0 | 0 | 0 |  |  | 0
risk assessor | What is the normal operating pressure of the main? |  | 0 | 0 | 0 | 0 | 0 |  |  | 0
|  | Severity / Consequence Score | [7 empty] | -5 |  | Severity Score
| Likelihood of Catastrophic Failure Questions | Pick from dropdown | [7 empty] | Score | [10 empty] | Risk Assessment Comments | Guidance
risk assessor | Is the work planned to be undertaken on (or in the vicinity of) a live main? |  | 0 | [6 empty] | -30 |  |  | Yes | No | N/a
risk assessor | What is the size of main being worked on (or we are adjacent to)? |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  | 0-6inch | 7-8inch | 9-12inch | 13-24inch | >24inch
risk assessor - add condition format for AC. Mitigation requirements | What is the pipe material? |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | DI | CI | PE | GRP | AC | UPVC | Steel
??? | Will there be any other mains within the excavation (or within 1m) which can not be isolated? |  | 0 | [6 empty] | 0 | [12 empty] | 0 | 0
nst view on eform | Are ground conditions understood prior to carrying out the work? |  | 0 | [6 empty] | 5 |  |  | 0-3bar | 4-6bar | 7-10bar | >11bar | N/A - Depressurised | [5 empty] | 0 | 0
nst view on eform | Do the ground conditions means there is an increase risk of failure of the asset (eg, voids) |  | 0 | [6 empty] | 5 | [9 empty] | Additional Mitigation requirements before work can proceed. |  |  | 0 | 0
risk assessor to answer - add a don’t know and change condition format to ensure mitigation if over 1.2m | Is there a specific temporary works design in place to carry out this work? |  | 0 | [6 empty] | 5 |  |  | 0-1.19m | 1.2m-2m | 2m-4m | >4m | Don't know | [6 empty] | 0
nst view on eform | Have we conclusively proved that the we know the main we are working on? |  | 0 | [6 empty] | 5 | [11 empty] | Ref the ES20 & BS5975
nst view on eform | Do we envisage the main to be encased in concrete or is the work to be undertaken in close proximity to thrust restraints? |  | 0 | [6 empty] | 0
risk assessor to ans | Has a condition assessment / NDT testing been carried out on the main? |  | 0 | [6 empty] | 0 | [9 empty] | 0
risk assessor | If Yes does it show a high risk of failure? |  | 0 | [6 empty] | 0
| Does the MSRA clearly identify the sequence of events and control measures required to recharge the main? | [8 empty] | 10
|  | Likelihood Score | [7 empty] | 0
-5
|  | likelihood | [7 empty] | 0
|  | likelihood | [7 empty] | 0
|  | severity | [7 empty] | -5
|  | severity | [7 empty] | 0
|  | Likelihood Score (max 60) | [7 empty] | 0 |  | Likelihood Score | [8 empty] | Comments Summary
|  | Severity Score (max 60) | [7 empty] | 0 |  | Severity Score
|  | high | [7 empty] | 0
|  | high | [6 empty] | 3257 | 0
|  | low | [7 empty] | 1
|  | low | [7 empty] | 1
|  | med | [7 empty] | 0
|  | med | [7 empty] | 0
Risk Level
LOW RISK
LOW RISK
0
Mitigation measures required before work can proceed.
SEVERITY 1. if it’s a tm and on tool what is the h&s score.
speak to ash to understand the stage 1, stage1a, ptw( stage1 and 1a are done by risk assessor and stage 2 is signed off by NOE
stakeholder to engage, Scot Wilkins, Mark Hancock, Stuart Smith.
Method Statement & Risk Assessment agreed by Thames Water site supervisor or where applicable, the site supervisor within the delivery partner organisationNetwork Optimisation Engineer or Risk Assessor to agree PTW content prior to issue.Any other mitigation measures identified on Risk Assessment TabMedium Isolation of the main should be considered in the first instance and must be discussed with the C Grade Area Manager. If this is not reasonably practicable, see Medium Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
Method Statement & Risk Assessment agreed by Thames Water site supervisor or where applicable, the site supervisor within the delivery partner organisation Network Optimisation Engineer or Risk Assessor to agree PTW content prior to issue.Any other mitigation measures identified on Risk Assessment Tab Medium Isolation of the main should be considered in the first instance and must be discussed with the C Grade Area Manager. If this is not reasonably practicable, see Medium Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
Note on D13: NB. This is depth to invert. Remember that, any excavation over 1.2m deep or adjacent to a live carriageway will require appropriate engineered support, “For all excavations at 1.2m depth proper assessments must be made and recorded prior to further excavation taking place.” See Essential Standard No1.

## Sheet3 (hidden)
–At what depth is the main? | 0-1.2m | 0-1.2m (1), 1.3-2 (2), >2m (3) | 0-1.2m | 1.3m-2m | 2m-4m | >4m
–IS public safety at risk if the main were to burst during the work. (schools, basements, railway lines, underground)? | No | yes (1) or no (2)
Will contigency measures be in place to mitigate the risk of flooding in the event of failure | N/a
–Have we conclusively proved that the we know the main we are working on.
–Do we envisage the main to be incased in concrete or is the work to be undertaken in close proximity to thrust restraints?
–Others?
water quality
pollution
ground conditions
Other info, eg booster stations, strategic assets, other tw work in the area.
Need to use the process to generate scenarios. ie, we can choose the least risky solution.
Need to be able to apply to waste RM
Age
Class
Trunk Mains
contaminated land
other services

## MITIGATION REQUIREMENT
Risk Level | Mitigation Measures Required Before Work Can Proceed
Low | Method Statement & Risk Assessment agreed by Thames Water site supervisor or where applicable, the site supervisor within the delivery partner organisation Network Optimisation Engineer or Risk Assessor to agree PTW content prior to issue. | Method Statement & Risk Assessment agreed by Thames Water site supervisor or where applicable, the site supervisor within the delivery partner organisation Network Optimisation Engineer or Risk Assessor to agree PTW content prior to issue.Any other mitigation measures identified on Risk Assessment Tab Medium Isolation of the main should be considered in the first instance and must be discussed with the C Grade Area Manager. If this is not reasonably practicable, see Medium Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
Any other mitigation measures identified on Risk Assessment Tab Medium Isolation of the main should be considered in the first instance and must be discussed with the C Grade Area Manager. If this is not reasonably practicable, see Medium Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
Medium | Method Statement & Risk Assessment for live working must be agreed by Thames Water Area Manager or where applicable, Area Manager within the delivery partner organisation and agreed with Thames Water responsible persons | Method Statement & Risk Assessment for live working must be agreed by Thames Water Area Manager or where applicable, Area Manager within the delivery partner organisation and agreed with Thames Water responsible personsA clear and adequate contingency plan for a burst main event must be identified in the Method StatementNetwork Optimisation Engineer or Risk Assessor to agree PTW content prior to issue (prior to any works taking place)Valve checks must be completed and method for isolating main confirmed in the event of a failure - A trial shut prior to work commencing MUST be considered if reasonably practicable - Any other mitigation measures identified on Risk Assessment Tab High Isolation of the main MUST be considered in the first instance and must be discussed with C Grade Area Manager. If this is not possible, see High Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
A clear and adequate contingency plan for a burst main event must be identified in the Method Statement
Network Optimisation Engineer or Risk Assessor to agree PTW content prior to issue (prior to any works taking place)
Valve checks must be completed and method for isolating main confirmed in the event of a failure - A trial shut prior to work commencing MUST be considered if reasonably practicable - Any other mitigation measures identified on Risk Assessment Tab High Isolation of the main MUST be considered in the first instance and must be discussed with C Grade Area Manager. If this is not possible, see High Risk Level control measures on "MITIGATION REQUIREMENT" TAB.
High | Method Statement & Risk Assessment for live working must be agreed by the Thames Water Senior Health and Safety Representative and where applicable, the Senior Manager within the delivery partner organisation A clear and adequate project specific contingency plan for a burst main event must be identified in the Method Statement and be agreed with the Senior Health and Safety Business Partner in Thames Water C Grade Area Manager to sign off PTW and confirm that full isolation and depressurisation is not possible Valve checks must be completed and method for isolating main confirmed in the event of a failure A trial shut prior to work commencing must be completed Any other mitigation measures identified in Comments boxes on Risk Assessment Tab | Method Statement & Risk Assessment for live working must be agreed by the Thames Water Senior Health and Safety Representative and where applicable, the Senior Manager within the delivery partner organisation A clear and adequate project specific contingency plan for a burst main event must be identified in the Method Statement and be agreed with the Senior Health and Safety Business Partner in Thames Water C Grade Area Manager to sign off PTW and confirm that full isolation and depressurisation is not possible Valve checks must be completed and method for isolating main confirmed in the event of a failure A trial shut prior to work commencing must be completed Any other mitigation measures identified in Comments boxes on Risk Assessment TabOperational Control to be consulted to consider if the works should be managed as an eventWater networks Senior Manager and TW Area H&S Business Partner to be informed to consider handover to Capital DeliverySenior Leadership Team sign off required
Operational Control to be consulted to consider if the works should be managed as an event
Water networks Senior Manager and TW Area H&S Business Partner to be informed to consider handover to Capital Delivery
Senior Leadership Team sign off required